Determination of well loss and aquifer loss of New Construction Deep Water well at

artesian aquifer in Khulna City, Bangladesh.

By Nazrul Islam* Md. Zahangir Alam and Md Minhaz Mahmud.

ABSTRUCT

This work studied the performance of water well installed as artesian aquifer in South Western Region of Bangladesh. The main activities were known to the properties of aquifer condition on that area. Well performance was also measured after development of water well. The well performance and aquifer performance were justified by Rorabaugh’s graphical methods. The total depth of drilling was 305m from the ground level. Drilling completed by Hydraulic Rotary Drilling Machine. The methods of drilling were Reverse circulation drilling method. Well performance is an important for a water well business industries because performance of well calculating the service period how much time it will be run extraction of water from that well. Similarly aquifer performance is another important function for water well business industry.

Keywords: Aquifer, Borehole, Discharge, Step drawdown test.

*Author for Correspondence E-mail:naz87kuet@yahoo.com, Telephone: +8804181985.

Affiliation: Md. Zahangir Alam, E-mail: z_alam63@yahoo.com, Md Minhaz Mahmud,

E-mail:tomnhz@gmail.com

1.0 INTRODUCTION

1.1 Background

Khulna, the industrial and port city, as well the third largest city of Bangladesh located in the south-west region and lies in the delta of Ganges. The city is stretched 15 kilometer along the bank of river Bhairab and Rupsha, covering the area of approximate 46 sq. km. The second largest seaport of the country Mongla is only 40 km away from the city. The water supply system of the city is based mainly on ground water generally abstracted from deep aquifer. Citizens in Khulna have been suffering from limited access to safe and potable water. Only 18% of total 1 million populations in the city have access to piped water supply and the rest resorts to alternative water sources such as river, pond, deep and shallow hand tube-well etc. Shallow tube well water often contains significant salinity. In order to improve safe potable28water supply to the city dwellers, Khulna Water Supply and Sewerage Authority (KWASA) has undertaken a project; Development of Water Supply System in Khulna City to produce 20.00 MLD water from ground through installation of production tube wells at different locations of the city.

1.2 Geological Condition

The Khulna City area consists of late Holocene to recent alluvium of the Ganges deltaic plain in north and tidal plain in south. Complexes of channels of fluvial/tidal origin, or natural levees, bars, swamps and plains like floodplain, deltaic plains, estuarine plains coastal plain constitute the Khulna City area. Channels (tidal as well as fluvial), natural levee, flood plain, flood basin, ox-bow lake, abandoned channels, bars, swamps/flood basins and estuarine plain have been recognized as geomorphologic units within the Khulna City. The area is composed of sand, silt and clay in various proportions with small amount of coarse sand, which is classified into seven litho-stratigraphic units from base to top.

1.3 Ground water Quality

Water samples were collected from 22 existing hand tube wells (3 shallow and 19 deep) located at different points within the Khulna City area. The deep tube wells range from 284 to 348 m while the shallow tube wells range from 88 to 132 m. The different parameters of the samples were tested in the laboratory to know the quality of water. The test result shows that the 19 deep monitoring wells contain chloride within WHO standard (250mg/L) while the 3 monitoring shallow wells contain chloride ranges from 2250 to 2500 mg/L which is much higher than the WHO standard. Other drinking water parameters such as iron (Fe), manganese (Mn), Magnesium (Mg), Calsium (Ca),Sulphate (So4), pH, Bicarbonate(HCO3), Sodium (Na), Nitrate (NO), Arsenic(As), Potassium (K) etc. are found within WHO and Bangladesh Standard for both deep and shallow aquifer. The shallow aquifer is severely affected by salinity intrusion from the costal river (Bhairab and Rupsha River) stretched along the east side the Khulna City.

1.4 Lithology

Exploratory drillings at 13 locations in the city were conducted under the project before main drilling starts to have idea about the formation lithology of the tube well sites. After that main drilling was conducted for installation of tube wells. The borehole lithology from the drilling, geophysical logging and previous drilling experience shows that the geological formation consists of a thick silty clay layer of about 115 m in between the shallow and deep aquifer at a depth from 120 to 235 m. The clay layer is basically resisting saline water intrusion and protection the water from saline contamination at deep aquifer.

2.0 MATERIALS AND METHODS

2.1 Exploratory Drilling

Exploratory drillings (Test drilling) to a depth of about 300m at production tube well locations were carried out manually by using 10 cm cutter and 38 mm MS pipe. Water as drilling fluid was circulated by mud pump directly during drilling. The drilling samples were collected at each of 1.5 m interval of borehole. The samples were analyzed through standard sieve set (#4, #8, #16, #30, #50, #100) in order to determine D60, D30, D10 and uniformity co-efficient (Cu) of the samples based on which grade of gravel pack, strainer slot size and tube well fixtures were designed for the tube well.

2.2 Main Drilling and Design of Wells

The main drillings were carried out by Hydraulic rotary drilling machine by using 50 cm cutter to a depth of 305 m. Based on the analysis of drilling samples, gravel pack material, strainer slot size and fixtures tube well (150 x 350 mm) were finally designed. Also Geo-physical loggings were also conducted to the bore holes to get idea about aquifer material and water quality which assisted to finally locate the strainer position in the borehole and the tube wells were also lowered accordingly. The tube well fixtures can generally are described as:

a. 	Upper Well Casing (350 mm)				37 m

b.	Reducer (150 x 350 mm)				01 m

c.	Lower Well Casing (150 mm)			230 m

d.	Strainer (20/ 30 Slot)					30 m

e.	Sand Trap						07 m

2.3 Well Development

Immediately after installation of the tube wells, following development activities to the wells were carried out:

- Development by airlifting using compressor

- Developing by high velocity water jetting

- Development by over pumping (3-steps)

- Development by over pumping was accompanied by chemical treatment with addition of calgon (Sodium Hexa Meta phosphate) and bleaching powder in each of the step.

2.4 Testing and Recovery

Both the step drawdown and long term testing were carried for each of the production tube well. The step drawdown tests were performed by pumping water at four variable rates for 8 hours (each step 120 minutes). The appointed data collectors recorded time, discharge, water level etc. at different stages of development. After completion of step drawdown test long term pumping test for 72 hours were carried time, discharge, water level etc. were also collected continuously for full period of pumping. Recovery of the aquifers was also monitored and data were recorded for the period of full recovery.

2.5 Determination of Aquifer and Well Loss & Well Efficiency

The test data were analyzed by a graphical solution to Jacobs equation developed by bruin Hudson, 1995 and by Rorabaugh’s method, 1953.The basic theory of step-draw down test analysis is provided below. The only pump that can give adequate information is the step drawdown test which was suggested by Jacob, 1947.Jacob noted that draw-down in a pumping well has two components. The first component, termed “aquifer or formation loss” arises from the “resistance” of the aquifer matrix to fluid flow. Aquifer loss is proportional to discharge Q and increases with time as the cone of influence expand. The second component, termed “well loss” represents the loss of head that accompany the flow through a well screen and in the casing to the pump intake. Jacob noted that well loss is proportional to the square of the discharge and is independent of times. The step drawdown test is the only test that can results in a function relationship between drawdown and discharge. He defined the following equation:

Sw = BQ+CQ2

Where:

Sw= Total drawdown in a pumping well (L).

Q= Pumping Rate (L3/t).

BQ= Component of drawdown due to aquifer/formation loss.

CQ2= Component of drawdown due to well loss.

B= Aquifer loss constant (T/L2). B represents the total resistance of the aquifer matrix from the well face out to the radius of influence.

C= well loss constant (t2/L5).

Well Efficiency (Ew):  The efficiency of a well, for a specified duration of pumping, is given by:

Specific capacity for the observed drawdown, Q/Sw

Ew  =	        							            X 100

Theoretical specific capacity, Q/BQ

Ew = (BQ/Sw) x 100 %

2.6 Calculation

Tested data Table1: PTW1

Fig. 1: Plot of Discharge against Sw/Q in well PTW1

Sw=BQ+CQ2

For firm line, Sw = (2.28x1.67+0.62x1.672) =3.8076+1.7291=5.54

Aquifer Loss= (3.81/5.54)x100=68.77%

Well Loss= (1.73/5.54)x100=31.23%

Well Efficiency (Ew) = (BQ/Sw) x 100 % = (2.28x2.75)/11.86x100%= 53%

Tested data Table2: PTW2

Fig. 2: Plot of Discharge against Sw/Q in well PTW2

Sw=BQ+CQ2

For firm line, Sw= (6.1x1.67+0.65x1.672) =10.187+1.813=12.00

Aquifer Loss= (10.187/12.00)x100=84.89%

Well Loss= (1.813/12.00)x100=15.11%

Well Efficiency (Ew) = (BQ/Sw) x 100 % = (6.1x2.0)/16.46x100% = 74%

Tested data Table: PTW3

Fig. 3: Plot of Discharge against Sw/Q in well PTW3

Sw=BQ+CQ2

For firm line, Sw= (4.72x1.67+.15x1.672) =7.882+2.7889=10.6709

Aquifer Loss= (7.88/10.67)x100=73.85%

Well Loss= (2.79/10.67)x100=26.15%

Well Efficiency (Ew) = (BQ/Sw) x 100 % = (4.72x2.43)/12.22x100% = 93% Tested data Table 4: PTW4

Fig. 4: Plot of Discharge against Sw/Q in well PTW4

Sw=BQ+CQ2

For firm line, Sw= (2.51x1.67+0.52x1.672) =4.1917+1.4502=5.6419

Aquifer Loss= (4.1917/5.6419)x100=74.30%

Well Loss= (1.4502/5.6419)x100=25.70%

Well Efficiency (Ew) = (BQ/Sw) x 100 % = (4.19x2.5)/10.85x100% = 96%

Tested data Table 5: PTW5

Fig.5: Plot of Discharge against Sw/Q in well PTW5

Sw=BQ+CQ2

For firm line, Sw= (5.97x1.67+0.26x1.672)=9.97+.73=10.70

Aquifer Loss= (9.97/10.70)x100=93.18%

Well Loss= (0.73/10.70)x100=6.82%

Well Efficiency (Ew) = (BQ/Sw) x 100 % = (5.97x2.33)/18.26x100% = 76%

RESULTS AND DISCUSION

Tables (1 to 5) show the value of step draw-down pumping test. Graphical values of the figure. (1 to 5) shows the value of well loss (BQ) and formation loss (CQ2). Here determined the value of B and C from Rorabaugh (1953) modified graphical method. The average values of well loss are about 7% to 31% and aquifer loss are about 67% to 93%. PTW2 and PTW5 well performance are very good and other three are poor development but reasonable. Below showing the summery of well loss, aquifer loss and Efficiency percentage:

Data sheet for Summery:

Fig.6: Bar shows the value percentage of Aquifer Loss, Well Loss & Efficiency.

CONCLUSIONS

The City of Khulna well sites founded high potential yield which supported the water supply authority to for water supply services. In this area ground water aquifer is artisan aquifer which support to well extraction percentage is very high quantity of water. In water well construction period should be very careful for using borehole wall forming materials. Development period will be conscious every technical person for proper way to develop the well then well loss come to satisfactory level.

ACKNOWLEDGEMENTS

The authors are wishes to express thanks to the Khulna WASA & BETS consulting Services Ltd for providing the computing facilities to carry out this work. Also appreciated is the research paper writing support received from Professional Hydro-geologist Vincent W. Uhl.

REFERENCES

Bierschenk,W.H.,1964.Determining well efficiency by multiple steps –drawdown tests.

Intl.Assoc.Sc. Hydrol.Publ., 64:493-507.

Cooper, H.H. and Jacob C.E 1946. “A generalized graphical method for evaluating formation constant and summarizing well field history.Trans.Amer Geophys. Union, 27:526-534.”

H. M Raghunath “Ground water -2nd edition”

Rorabaugh M.I 1953. Graphical and theoretical analysis of step drawdown test of artesian well.proc.sep. Number 362 volume 79 ASCE.

Vincent W. Uhl and Anthony J Rana. “Application of Step drawdown pumping tests in consolidated rock aquifer”